# General

### Not Used

# Products

## General Requirements

### Design fire and life safety systems in accordance with the requirements of the BC Building Code, the BC Fire Code, and the National Fire Protection Agency.

### Refer to CSA Z317.1 for fire-protection requirements.

## Fuel Systems

### Only the following fuel tank configurations are acceptable:

#### Freestanding tank inside a building in a concrete vault with a containment wall.

#### Above-grade tank outside a building, located to minimize risk of damage from floods or wildfires where applicable.

#### Below-grade free standing tank boxed in a pre-cast concrete vault (instead of fully direct buried) with removable slab lids, access manhole with ladder and full maintenance access around the tank.

### Provide a fuel polishing system that meets SAE J1488 2010 filtration specifications.

### Provide fuel measurement and leak detection system for bulk fuel storage systems.

# Execution

### Not Used

END OF SECTION