# General

### Not Used

# Products

## Motor Protection and Control

### Group motor starters in common areas within mechanical or electrical rooms.

### Utilize motor control centres (MCCs) for groups of four or more motors that require individual motor starters. Provide individual enclosed motor starters for individual motors.

### Provide labelling on MCC’s to match motors.

### Starters to be National Electrical Manufacturers Association (NEMA) rated.

### Do not use fuses for individual motor overcurrent protection.

### Provide single phase protection for all three phase motors either by relaying, or differential overloads.

# Execution

### Not Used

END OF SECTION