# General

### Not Used

# Products

## Transfer Equipment

### Provide closed transition, soft load transfer design that utilizes a draw out air circuit breaker transfer scheme with bypass breakers for redundancy and servicing without the interruption of power.

#### Shall have interlocks and tie breaker to increase redundancy.

### Shall have adjustable base load design for annual load test requirements.

### Provide elevator pre-transfer signaling feature for use in test mode, with manual bypass option for operators control choice.

### Make provisions for connections to an external load bank or generator to facilitate repairs and testing.

# Execution

## Installation

### Locate transfer equipment and main emergency distribution in close proximity to (but not within) emergency generator room.

END OF SECTION