# General

### Not Used

# Products

## General

### Provide surge protective devices (SPD’s) either integral buss mounted or separate mounted on the distribution equipment. Coordinate suppression with anticipated energy levels and sensitive loads.

### Provide surge suppression in one of the following manners:

#### Level 1: Install surge suppression on utility incoming mains.

#### Level 2: For areas containing a large group of electrically sensitive loads, provide surge protection on panelboards serving the area.

#### Level 3: Provide individual pieces of sensitive equipment, not otherwise protected, with local surge suppression module (computer power bar or wall plug-in style – not part of the construction budget).

### Level 1 & 2 surge protectors to have built in monitoring with alarm points to the PME (Power Monitoring Expert)

### Coordinate surge protective devices within the same power distribution system.

### Provide, as a minimum, Level 1 SPDs in all buildings.

### Provide a disconnecting means for each surge protective device to allow servicing or replacement without an outage to the bus where it is connected.

# Execution

### Not Used

END OF SECTION